Cooling Tower Maintenance Program and Plan Template

Version: 1.0

New York State Department of Health

Bureau of Water Supply Protection

August 2017

# Introduction

This document is designed as a guide to the development of a maintenance program and plan for a cooling tower. The sections included in this template represent a survey of procedures currently used in the field and aim to capture the essential building blocks required for a comprehensive program document. The sections included serve as guidance and are therefore not specified by Subpart 4-1 of the New York State Sanitary Code.

The complete text of the regulation can be found here: https://regs.health.ny.gov/content/part-4-protection-against-legionella.

# Disclaimer

This is a suggested template for a maintenance program and plan required by Subpart 4-1 of the New York State Sanitary Code.  The examples provided should not be considered as recommendations from the New York State Department of Health for treatment options. This material should be considered the minimum suggested information used to define the maintenance program and plan; each cooling tower and situation is unique and an expansion of elements on a case by case basis may be required.

Cooling Tower Maintenance Program and Plan Template

Prepared for:

Prepared by:

Effective Date:

# Contents

Section 1.	Facility Information	4

1.1	Cooling Tower Location	4

1.2	Developer of Maintenance plan (company)	4

1.3	Effective Date of Maintenance Plan	4

1.4	Cooling Tower Information	4

1.5	Additional narrative:	5

Section 2.	Process Description	6

2.1	Tower System Description	6

2.1.1	Filter information (if used)	6

2.2	Process Schematic	7

2.3	Heat source Description	7

2.4	Control Elements	8

Section 3.	Personnel Roles and Responsibilities	9

3.1	Personnel	9

3.2	Responsibilities and Roles	10

Section 4.	Program Validation	12

Section 5.	Program Implementation	13

5.1	Program Chemistry	13

5.1.1	Corrosion inhibitors	13

5.1.2	Biocides/disinfectants	13

5.1.3	Dispersants/detergents	13

5.2	Program Materials	13

5.3	Program Testing/Sampling Devices	13

5.3.1	Program Chemical Testing	14

5.3.2	Program Bacterial culture devices (e.g. Dipslides)	14

5.4	Program Administration Equipment	14

5.4.1	Data generation/Sampling & Control	14

5.4.2	Control Elements	14

Section 6.	Onsite Monitoring Procedures	15

6.1	Monitoring Schedule	15

6.2	Monitoring Methods and Procedures	15

6.3	Monitoring Response Protocols	16

6.4	Monitoring Log	16

Section 7.	Onsite Maintenance Operations	17

Section 8.	Cooling Tower Operation Procedures	18

8.1	Season Startup Procedure	18

8.2	Season Shutdown Procedure	18

8.3	Non-load Operation/Procedure	18

8.4	Temporary Shutdown and Startup for Maintenance Operations	18

8.5	Cooling Tower Cleaning Procedure	18

8.6	Cooling Tower Online Disinfection Procedure	18

8.7	Cooling Tower Emergency Disinfection Procedure	18

8.8	Cooling Tower Cleaning Procedures	18

8.9	Commissioning Guidelines For new Cooling Tower Systems	19

8.10	Contingency Cooling for Planned or Unplanned Tower Interruptions	19

8.11	Contingency Response Plan, System Interruptions	19

8.12	Side Stream Filter Maintenance and Disinfection Procedures	19

8.13	Circulation Procedure for Off Line/Idle	19

Section 9.	Biological Sampling Plan	20

9.1	Frequency of Routine Biological Sampling	20

9.2	Biological Sampling Required Due to Operational Issues or Epidemiological Concerns				20

Section 10.	Maintenance Responses to Testing	21

10.1	Interpretation of Legionella Culture Results from Cooling Towers	21

Section 11.	Maintenance, Culture and Disinfection Reports	23

11.1	Microbiological Testing Reports	23

11.1.1	Bacteria	23

11.1.2	Legionella	23

11.2	Inspection Reports	23

11.3	Cooling Tower Cleaning Reports	23

11.4	Online Disinfection/Decontamination Reports	23

11.5	Maintenance Reports	23

11.5.1	Routine	23

11.5.2	Remedial	23

11.6	Annual Inspection Reports	23

Section 12.	Chemical Supply Log	24

12.1	Resupply Log for Biocide	24

12.2	Resupply Log for Corrosion Inhibitor	24

12.3	Resupply Log for Anti-scalant Agent	24

12.4	Other Materials That May Be Used for Cooling Tower Maintenance and Operation	24

Section 13.	Cut Sheets for Program Equipment	25

Section 14.	Appendix A	26

# Facility Information

[This section includes a description of the facility’s information.]

## Cooling Tower Location

[Provide information on the cooling tower location.]

| Owner name |  |
| --- | --- |
| Point of contact name |  |
| Point of contact phone |  |
| Street address |  |
| Building name (if applicable) |  |
| City, town, or village |  |
| County |  |
| Latitude-longitude (if available) |  |

## Developer of Maintenance plan (company)

[Provide information on the developer of the maintenance plan.]

| Company name |  |
| --- | --- |
| Point of contact name |  |
| Point of contact title |  |
| Point of contact phone (office) |  |
| Point of contact phone (mobile) |  |
| Email address |  |
| Street address |  |
| City, state, ZIP code |  |

## Effective Date of Maintenance Plan

[Record the date the maintenance plan goes into effect.]

| Date |  |
| --- | --- |

## Cooling Tower Information

[The following information is typically available from the design drawings, operation information and/or on the tower itself.]

| Manufacturer of cooling tower |  |
| --- | --- |
| Model number of cooling tower |  |
| Serial number of cooling tower |  |
| Registration number from New York State Registry |  |
| Year commissioned |  |
| Thermal cooling capacity of cooling tower |  |
| Cooling tower type (e.g. cooling tower, evaporative cooler, evaporative condenser, etc.) |  |
| Description of the process from which heat is being removed |  |
| Water source (e.g., municipal water company, onsite) |  |
| Water disposal method (sanitary sewer company, onsite disposal, discharge by permit to the environment, etc.) |  |

## Additional narrative:

[Add any additional narrative that may be used to augment the information that was recorded in Section 1.1 above.]

# Process Description

[This section includes the mechanical and quantitative description of the cooling tower process.]

## Tower System Description

[Provide a description of the tower system]

| Tower type and design |  |
| --- | --- |
| Configuration |  |
| Purpose |  |
| Component the tower is attached to |  |
| Operational period type (e.g. seasonal, year long, as needed, etc.) |  |
| Typical operational season (start date to end date) |  |
| Number of days per week tower is used |  |
| Number of weeks per year the tower is used |  |
| Total system water volume (both basin and the water that is contained in the piping) |  |
| Cooling capacity (Tons, BTU/hr, etc.) |  |
| Circulation rate (either from basin to the spray deck or from basin and to the heat exchanger and to the spray deck, gpm) |  |
| Filtration used (yes/no) |  |

### Filter information (if used)

| Filter flow rate |  |
| --- | --- |
| Filter manufacturer |  |
| Filter model |  |
| Filter pump model |  |
| Filter pump maximum flow rate |  |
| Filter pump power (single or three phase) |  |
| Filter pump flow rate determined by flow controller or un controlled |  |
| Filter cleaning method (e.g. backwash, cartridge cleaning, bag replacement, etc.) |  |
| Pressure drop at which filter should be backwashed/cleaned etc. |  |

## Process Schematic

[Provide a schematic that contains sufficient information to provide a means of understanding the entire process and its mechanical components.]

Process Schematic Example

## Heat source Description

[Provide descriptions of: a) the source of the heat that is removed by the cooling tower; and b) how the loss of cooling equipment will be addressed by backup processes or methods.]

## Control Elements

[Designate the location and function of the control locations (or elements) that are used to maintain the operating variables of a cooling tower. Use the table below as the location for these data.]

Control element designation examples

| Control element | Control sensor | Purpose |
| --- | --- | --- |
| Bleed valve located on the bottom of the basin piping | Conductivity sensor located in control room. Solenoid valve is opened by signal from central control system | Allow water containing excessively high dissolved solids concentrations to be removed from the system to be replaced by fresh water. |
| Sand filter | Turbidity sensor used during maintenance visits | The sand filter is operated continuously on a circulation to filtration ratio that is established manually by valving and is checked periodically to ensure water turbidity is maintained. |
| Biocide pumps (halogen) | ORP sensor located in mechanical control room | On-line disinfection is maintained using ORP as the process variable to ensure there is adequate disinfectant maintained in the system. |
| Biocide pumps (non-halogen) | Periodic dip slide tests performed for feedback data | Bacteria counts are used as a means of measuring the effectiveness of the biocide process. |
| pH chemical feed pump | pH sensor located in mechanical control room | The pH of the water is used to protect the cooling tower components from corrosion. The pH of the water is maintained by the addition of xyz solution. |
| Antiscalant/corrosion inhibitor chemical feed pump | Chemical testing performed during periodic maintenance visits | The chemical feed pump dosing is adjusted based on test data during site visits. |

# Personnel Roles and Responsibilities

[This section includes the information of the of the personnel involved in the maintenance and operation of a cooling tower and the specific actions/activities to be performed by those personnel.]

## Personnel

[Record the information of the personnel involved in the maintenance and operation of a cooling tower.]

Maintenance program administrator

| Name |  |
| --- | --- |
| Title |  |
| Employer or company |  |
| Address |  |
| Phone number |  |
| Email address |  |

Licensed pesticide applicator

| Name |  |
| --- | --- |
| Pesticide applicator New York State DEC license number (7G) |  |
| Employer or company |  |
| Address |  |
| Phone number |  |
| Email address |  |

Maintenance personnel (provide information for each individual)

| Name |  |
| --- | --- |
| Title |  |
| Employer or company |  |
| Address |  |
| Phone number |  |
| Email address |  |

Maintenance program validator

| Name |  |
| --- | --- |
| Title |  |
| Employer or company |  |
| Address |  |
| Phone number |  |
| Email address |  |

## Responsibilities and Roles

[This section outlines actions/activities to be performed in accordance with 10NYCRR 4-1.]

| Responsibility/Role | Frequency Performed | Person/Company |
| --- | --- | --- |
| Cooling tower registration | Once when commissioned. |  |
| Reporting | Intervals of no more than 90 days. |  |
| Development and updating of required maintenance program and plan | As needed. |  |
| Bacteriological culture sampling | Intervals not to exceed 30 days while the cooling tower is in use, and that requires additional bacteriological culture sampling and analysis, as needed, to validate process adjustments. |  |
| Legionella culture analysis | Within two weeks after startup and after maintenance shutdown and at intervals not to exceed 90 days while the cooling tower is in use. |  |
| Immediate and appropriate actions specified by Appendix 4-A | Immediate and appropriate actions that are in response to bacteriological and Legionella culture analysis. |  |
| Notification | In response to a Legionella result that exceeds 1,000 CFU/mL. |  |
| Disinfection | In response to a Legionella result that exceeds ≥ 20 CFU/mL. |  |
| Inspection | Inspection is required prior to seasonal start-up and at intervals not exceeding every 90 days while in use. Year-round towers are required to be inspected at intervals not exceeding every 90 days and prior to start-up following a maintenance procedure. |  |
| Certification | Annual certification is required by November 1 of each year. The certification document should attest that the cooling tower has a maintenance program and plan, and that all activities within that plan or required by the regulation were implemented. |  |
| Recordkeeping | Records of all sampling and analyses, disinfection schedules and applications, inspection finding, deficiencies, and corrective actions and certifications are required to be maintained for three years. |  |
| Checking chemistry levels in the tower | Frequency to be determined by the water treatment professional. |  |
| Checking the inventory of chemicals used to treat the tower water | Frequency to be determined by the water treatment professional. |  |

# Program Validation

[Program validation should be performed by an individual who has management responsibilities for the proper implementation of the maintenance program and plan to ensure all required activities are being properly executed. This section should identify the items to be examined and the frequency of the review.

The program validation procedure is performed by reviewing the data and maintenance logs to ensure: 1) the maintenance program is being executed as documented; 2) the maintenance program is effective at reaching its goals; and 3) deficiencies or unneeded components of the maintenance program are identified for correction in future revisions of the plan.]

Items and materials used for process validation

| Item examined | Purpose | Frequency |
| --- | --- | --- |

# Program Implementation

[A treatment program consists of the implementation of chemicals, testing/sampling systems and administration equipment. The following sections specify appropriate information. For example:

- Chemical(s) used for corrosion control

- Chemical(s) used for microbiological control

- Chemical(s) used for pH adjustment/maintenance

- Chemical(s) used for dispersants/penetrants

- Chemical(s) used for antiscalants

The information included in these sections should corroborate the process information in Section 2.4]

## Program Chemistry

[Provide information on program corrosion inhibitors, biocides/disinfectants, and dispersants/ detergents]

### Corrosion inhibitors

| Product | Manufacturer | NYS DEC Registration Number | Setpoint Range |
| --- | --- | --- | --- |

### Biocides/disinfectants

| Product | Manufacturer | NYS DEC Registration Number | Setpoint Range |
| --- | --- | --- | --- |

### Dispersants/detergents

| Product | Manufacturer | NYS DEC Registration Number | Setpoint Range |
| --- | --- | --- | --- |

## Program Materials

[Provide a list of those items and materials that are used in the water treatment program execution.]

| Item 1 |  |
| --- | --- |
| Item 2 |  |
| Item 3 |  |

## Program Testing/Sampling Devices

[Provide information on program chemical testing and bacterial culture devices.]

### Program Chemical Testing

| Product/Instrument | Manufacturer | Chemical Tested | Model Number |
| --- | --- | --- | --- |

### Program Bacterial culture devices (e.g. Dipslides)

| Product | Manufacturer | Model Number |
| --- | --- | --- |

## Program Administration Equipment

[The program and plan administration requires measuring water parameters such as conductivity, pH, oxidation-reduction potential (ORP) and other items vital to maintain the chemistry of the system.]

### Data generation/Sampling & Control

[Input the data generation/sampling and control equipment used to maintain the chemistry levels required by the program and plan.]

| Model | Quantity Measured | Sensor Manufacturer | Controller |
| --- | --- | --- | --- |
|  | Conductivity |  |  |
|  | ORP |  |  |
|  | pH |  |  |

### Control Elements

[Process variables may be maintained by electronic feedback loop or manual adjustment based on a test result. The following table captures the data that specify how variables are controlled.]

| Quantity Controlled | Element | Manufacturer | Model |
| --- | --- | --- | --- |
| Conductivity | Bleed valve |  |  |
| ORP | Chemical feed pump |  |  |
| Anti-scalant/corrosion inhibitor | Chemical feed pump |  |  |
| pH | Chemical feed pump |  |  |

# Onsite Monitoring Procedures

[Onsite monitoring is required to maintain the automated process monitoring and control systems, to check the effectiveness of the current set points and to adjust (if necessary) the open-loop control systems.]

## Monitoring Schedule

[List the monitoring schedule.]

| Operating variable | Monitoring activity | Frequency performed |
| --- | --- | --- |

## Monitoring Methods and Procedures

[Document the variables or parameters that are monitored and the procedure used to obtain process data. This section must be consistent with the information in Section 5.4.1.]

| Monitored variable | Procedure |
| --- | --- |
| Cooling tower water conductivity measurement |  |
| Cooling tower influent temperature |  |
| Cooling tower effluent temperature |  |
| Disinfectant test procedure |  |
| pH test procedure |  |
| Cooling tower bacteria sampling protocol |  |
| Cooling tower legionella sampling protocol |  |
| Disinfectants |  |
| Corrosion inhibitor/antiscaling agent |  |
| pH adjustment chemical |  |
| Pump operation validation |  |

## Monitoring Response Protocols

[List the responses to the results that are a result of the cooling tower measurements.]

| Variable | Acceptable range or limiting value | Procedure to address out-of-specification values |
| --- | --- | --- |
| Conductivity |  |  |
| pH |  |  |
| Biocide |  |  |
| Bacteria |  |  |
| Legionella |  |  |
| Temperature |  |  |
| Air flow rate |  |  |

## Monitoring Log

[Include the cooling tower monitoring sheets. The log must be consistent with the Maintenance Program and Plan that is developed by the cooling tower operator. The log sheets are therefore customized to the specifications of the program and plan.]

# Onsite Maintenance Operations

[Document the maintenance procedures that are required to be performed as a matter of routine operation of the cooling tower. Examples of routine procedures include calibration and cleaning of conductivity, pH and ORP probes, cleaning of the basin to maintain proper flow of water, water strainer cleaning and more.]

| Procedure name | Description of method |
| --- | --- |
| Sensor calibration |  |
| Basin cleaning |  |
| Filling chemical feed reservoirs |  |
| Additional regular maintenance |  |

# Cooling Tower Operation Procedures

## Season Startup Procedure

[Outline the tower startup procedure and specify all chemicals and/or cleaning agents used during the startup process.]

## Season Shutdown Procedure

[Outline the tower shutdown procedure and specify any and all chemicals and/or materials used for tower shutdown procedures.]

## Non-load Operation/Procedure

[Outline any and all differences in the operational procedure for running a cooling tower without any heat load.]

## Temporary Shutdown and Startup for Maintenance Operations

[Outline the shutdown and startup procedures that are associated with short term (temporary) conditions that are often associated with maintenance operations.]

## Cooling Tower Cleaning Procedure

[Describe procedure]

## Cooling Tower Online Disinfection Procedure

[Describe procedure]

## Cooling Tower Emergency Disinfection Procedure

[Describe procedure]

## Cooling Tower Cleaning Procedures

[Describe procedures]

## Commissioning Guidelines For new Cooling Tower Systems

[List guidelines]

## Contingency Cooling for Planned or Unplanned Tower Interruptions

[Describe contingency]

## Contingency Response Plan, System Interruptions

[Describe contingency]

## Side Stream Filter Maintenance and Disinfection Procedures

[Describe procedures]

## Circulation Procedure for Off Line/Idle

[Describe procedure]

# Biological Sampling Plan

[The following outline lists the minimum required sampling that must be performed to satisfy the requirements of Section 4-1.4.]

Frequency of Routine Biological Sampling:

- Bacteriological culture sampling

  - Not to exceed 30 days

- Legionella culture sampling

  - Within two weeks after the tower startup

  - Intervals not to exceed every 90 days while operational

  - Note: year-round operation requires sampling every 90 days as well as a sample within two weeks after start-up following maintenance

Biological Sampling Required Due to Operational Issues or Epidemiological Concerns:

- Legionella culture sampling and analysis

  - Power failure of sufficient duration to allow for the growth of bacteria

  - Loss of biocide treatment of sufficient duration to allow for the growth of bacteria

  - Failure of conductivity control, or any other control methods, to maintain proper cycles of concentration

  - Determination by the State Department of Health or the local health department that one or more cases of legionellosis is or may be associate with the cooling tower

  - Any other conditions specified by the Department or local health department

# Maintenance Responses to Testing

[The following table summarizes the requirements of Subpart 4-1 Appendix 4-A. Log the operational changes in response to non-compliant testing results.]

## Interpretation of Legionella Culture Results from Cooling Towers

| Interpretation of Legionella Culture Results from Cooling Towers |  |
| --- | --- |
| Legionella Test Results in CFU/mL1 | Approach |
| No detection (< 20 CFU/mL) | Maintain treatment program and Legionella monitoring in accordance with the maintenance program and plan. |
| For levels at ≥ 20 CFL/mL but < 1,000 CFL/mL perform the following: | - Review the treatment program. - Institute immediate online disinfection2 to help with control - Retest the water in 3-7 days. - Continue to retest at the same time interval until one sample retest result is < 20 CFU/mL. With receipt of a result <20 CFU/mL, resume routine maintenance program and plan. - If retest is ≥ 20 CFU/mL but < 100 CFU/mL, repeat online disinfection2 and retest until < 20 CFU/mL attained. - If retest is ≥ 100 CFU/mL but < 1000 CFU/mL, further investigate the water treatment program and immediately perform online disinfection2. Re-test and repeat attempts at control strategy until < 20 CFU/mL attained. - If retest is ≥ 1000 CFU/mL, undertake control strategy as noted below. |
| For levels ≥ 1,000 CFU/mL perform the following: | - Review the treatment program and provide appropriate notifications per section 4-1.6 of the regulation. - Institute immediate online decontamination3 to help with control - Retest the water in 3-7 days. - Continue to retest at the same timer interval until one sample retest result is < 20 CFU/mL. With receipt of a result <20 CFU/mL, resume routine maintenance program and plan. - If any retest is ≥ 20 CFU/mL but < 100 CFU/mL, repeat online disinfection2 and retest until < 20 CFU/mL attained. - If retest is ≥ 100 CFU/mL but < 1000 CFU/mL, further investigate the water treatment program and immediately perform online disinfection2. Re-test and repeat attempts at control strategy until < 20 CFU/mL attained. - If any retest is ≥ 1000 CFU/mL: - Carry out system decontamination4. |
| 1 Colony forming units per milliliter 2 Online disinfection means-Dose the cooling tower water system with either a different biocide or a similar biocide at an increased concentration than currently used. 3 Online decontamination means – Dose the recirculation water with a halogen-based compound (chlorine or bromine) equivalent to at least 5 milligrams per liter (mg/L) or parts per million (ppm) free residual halogen for at least one hour. 4 System decontamination means – Maintain between 5 to 10 mg/L (ppm) free residual halogen for a minimum of one hour; drain and flush with disinfected water; clean wetted surface; refill and dose to 1 – 5 mg/L (ppm) of free residual halogen and circulate for 30 minutes. Refill, reestablish treatment and retest for verification of treatment. For chlorine treatment the pH range should be 7.0 to 7.6; for bromine treatment the pH range should be 7.0 to 8.7. At higher pH values the treatment times may need to be extended. NOTE: Stabilized halogen products should not be used for online decontamination or system decontamination as defined in this Appendix per footnotes 3 and 4. |  |

# Maintenance, Culture and Disinfection Reports

[In this section, the service reports should be filed in chronological order. This section should not include responses to bacteriological or Legionella testing procedures.]

## Microbiological Testing Reports

### Bacteria

### Legionella

## Inspection Reports

## Cooling Tower Cleaning Reports

## Online Disinfection/Decontamination Reports

## Maintenance Reports

### Routine

### Remedial

## Annual Inspection Reports

# Chemical Supply Log

[Document records of restocking chemicals as a means of tracking the amount of material used for proper management of the water quality of the tower water. The tables shown below are examples of what should be documented for each product used in the maintenance program.]

## Resupply Log for Biocide

[Insert the biocide resupply log]

| Item | Resupply date | Quantity |
| --- | --- | --- |

## Resupply Log for Corrosion Inhibitor

[Insert the biocide resupply log]

| Item | Resupply date | Quantity |
| --- | --- | --- |

## Resupply Log for Anti-scalant Agent

[Insert the biocide resupply log]

| Item | Resupply date | Quantity |
| --- | --- | --- |

## Other Materials That May Be Used for Cooling Tower Maintenance and Operation

[Add any additional materials that may be used for cooling tower maintenance and operation.]

# Cut Sheets for Program Equipment

[Include the equipment that is used for executing the program and the specific model identified on the document.]

# Appendix A

[Use this section to document other items that are needed to define the maintenance program and plan.]

Registration is required by 10NYCRR 4-1.3(a)

Reporting of various test data and operations schedule is required by 10NYCRR Section 4-1.3(b).

The maintenance program and plan are required to be developed and implemented by September 1, 2016 by 10NYCRR Section 4-1.4(a).

Bacteriological culture sampling is required by 10NYCRR Section 4-1.4 (b)(1).

Legionella culture sampling is required by 10NYCRR Section 4-1.4 (b)(2).

10NYCRR Section 4-1.4 (b)(4) requires immediate and appropriate actions in response to bacteriological and Legionella culture analyses that exceed values that are stipulated in Appendix 4-1-A. See Appendix 4-1-A for more details of appropriate actions.

Notification of the local health department within 24 hours of receipt of a Legionella culture sample result that exceeds 1,000 colony forming units (CFU) per milliliter is required by 10NYCRR Section 4-1.6 (a). Notification of the public may also be required as determined by the local health department (10NYCRR Section 4-1.6 (b)).

Disinfection is required by 10NYCRR Section 4-1.7 (a) to be performed by a pesticide applicator who is certified in accordance with the requirements of Article 33 of the Environmental Conservation Law and 6 NYCRR Part 325, or a pesticide apprentice under the supervision of a certified applicator.

Inspection is required by 10NYCRR Section 4-1.9.

Certification are required by 10NYCRR Section 4-1.9.

Record keeping is required by 10NYCRR Section 4-1.9.